PART 1 GENERAL

  - REFERENCES

A.	AMCA 500 - Test Methods for Louvers, Dampers and Shutters.

B.	AMCA 511 - Certified Ratings Program for Air Control Devices.

  - SUBMITTALS

A.	Submit manufacturer's product data.

1.	Include leakage, pressure drop, and maximum pressure data.

2.	Indicate materials, construction, dimensions, and installation details.

3.	Verify damper leakage rating AMCA certified.

4.	Verify damper pressure drop ratings based on tests and procedures performed in accordance with AMCA 500.

  - QUALITY ASSURANCE

- Damper Capacity:  Demonstrate damper capacity to withstand HVAC system operating conditions.

- Pressure Drop Ratings:  Damper pressure drop ratings based on tests and procedures performed in accordance with AMCA 500.

- Leakage Rating:  Damper leakage rating AMCA certified (K-RD-503 & K-RD-504 only).  Damper licensed to bear AMCA Certified Ratings Seal in accordance with AMCA 511. AMCA Certified Ratings Seal applies to air leakage performance.

  - DELIVERY & STORAGE

- Delivery: Deliver materials to site in manufacturer's original, unopened containers and packaging, with labels clearly indicating manufacturer and material.

- Storage: Store materials in a dry area indoors, protected from damage and in accordance with manufacturer's instructions.

- Handling: Handle and lift dampers in accordance with manufacturer's instructions. Protect materials and finishes during handling and installation to prevent damage.

PART 2 PRODUCTS

  - MANUFACTURER

A.	M.K. Plastics Corporation, model K-RD-501, K-RD-502, K-RD-503, K-RD-504 or equivalent.

  - FIBERGLASS ROUND CONTROL DAMPERS

- Damper frame shall be of one piece construction with a resin rich interior corrosion barrier minimum of 100 mills. A structural lay-up shall consist of alternate layers of chopped strand mat and woven roving to conform to ASME/ANSI ATP-1 and ASTM D3982. The glass to resin ratio shall be a minimum of 35% glass to 65% resin. Wall thickness, flange thickness, drilling pattern and width shall conform to ASTM D3982 Table 1.

- Exterior surface of the damper shall contain UV inhibitors and a gelcoat, standard color shall be M.K. Plastics Light Gray.

- The damper blade shall be constructed of the same material as the damper frame and shall have a resin rich surfacing veil on both sides. Blade stiffeners shall be FRP or FRP encapsulated as required for stiffness.

- The axles shall be 304 or 316 stainless steel or pultruded FRP as required to meet corrosion resistance requirements.

- Leakage shall not exceed 3 cfm per square foot at 12” w.g. or 5.25 cfm per square foot at 30” w.g. as required in this specification for isolation.

- Damper shall be provided with stainless steel hand locking quadrant, gear operators, chain wheel operators, or other actuation devices as required in this specification.

- All interior metal shall be 304 or 316 stainless steel. Gaskets shall be EPDM. Other gasket materials shall be available upon request.

- All FRP fabrication shall meet or exceed quality requirements of ASTM D 3982 and ASME/ANSI ATP-1.

PART 3 EXECUTION

3.1  EXAMINATION

- Inspect areas to receive dampers.  Notify the Engineer of conditions that would adversely affect the installation or subsequent utilization of the dampers. Do not proceed with installation until unsatisfactory conditions are corrected.

3.2  INSTALLATION

- Install dampers at locations indicated on the drawings and in accordance with manufacturer's installation instructions.

- Install dampers square and free from racking with blades running [horizontally] [vertically].

- Do not compress or stretch damper frame into duct or opening.

- Handle damper using [sleeve or] frame. Do not lift damper by the blades, actuator or jackshaft.

- Install bracing for multiple section assemblies to support assembly weight and to hold against system pressure. Install bracing as needed.