PART 1  GENERAL

1.01 WORK INCLUDED

- Fiberglass Reinforced Plastic (FRP), Bifurcated Inline Centrifugal Fans.

1.02 RELATED WORK

- All sections, drawing plans, specifications and contract documents.

1.03 REFERENCES

- AMCA -99 Standards Handbook

- AMCA 210 - Laboratory Methods of Testing Fans for Rating Purposes.

- AMCA 211 - Certified Ratings Procedure.

- AMCA 300 - Test Code for Sound Rating Air Moving Devices.

- AMCA 311 - Certified Sound Ratings Program for Air Moving Devices.

- AFMBA - Method of Evaluating Load Ratings of Bearings (ASA - B3.11).

- AMCA 204 - Balance Quality and Vibration Levels for Fans.

1.04 QUALITY ASSURANCE

- Performance ratings: Conform to AMCA standard 211 and 311.

- Classification for Spark Resistant Construction Conform to AMCA 99.

- Each fan shall be tested before shipping.  Motors to be tested for amperage draw.

- A certificate shall be supplied for each fan, certifying quality control and compliance to  specifications, prior to shipping.

1.05 SUBMITTALS

- Provide dimensional drawings and product data on each fan assembly.

- Provide fan curves for each fan at the specified operation point, with the flow, static pressure and horsepower clearly plotted.

PART 2  PRODUCTS

2.01 GENERAL

- Base fan performance at standard conditions (density 0.075 Lb/ft3 ).

- Fans selected shall be capable of accommodating static pressure and flow variations of +/-15% of scheduled values.

- Each fan shall be belt or direct driven in AMCA arrangements as stated in the specs or on the drawings.

- Fans to be equipped with lifting lugs.

- Motor mounting plate / bearing mounting plate to be coated steel with a minimum of 4-6 mils of chemical resistant epoxy.

- Fasteners to be 304 stainless steel.

- UV inhibitors are added to the resins and are flame retardant class 1 of 25 or less.

2.02 FAN HOUSING

- Fan housing shall be of the bifurcated design, in which all impeller drive components are outside of the corrosive, contaminated air stream. Housing as well as air inlet shall be aerodynamically designed for  high-efficiency, engineered to reduce incoming air turbulence. Housings shall be resin rich to be smooth exterior and interior.

- Fan housing shall be manufactured in specifically formulated resins, for maximum corrosion resistance, and reinforced with fiberglass for structural strength. Fastening bolts holding the casing to the support plate are to be encapsulated in FRP. No uncoated metal fan parts in the corrosive air stream will be tolerated.

- Fans shall be supplied with a internal graphite liner and grounding strap to remove static electricity, if scheduled.

- For horizontal airflow applications, a casing drain for condensation removal shall be an integral part of the fan housing, and attached to the casing at the lowest point.

- Fan inlet & outlet to be slip connections or flanged.

- A housing access door shall be supplied for impeller inspection and service.

- Hub seal to be neoprene or Teflon (when required).

- AXCL fans shall be supplied with horizontal or vertical mounting brackets, if stated and shown on the plans and specifications.

- Roof mounted fans shall be supplied with FRP curb caps and discharge butterfly dampers, if stated and shown on the plans and specifications.

- M. K. Plastics (when specified) will supply a Vacuum Hub Seal to avoid any contaminated air from escaping (patent pending)

- Finish color to be light gray.

2.03 FAN IMPELLER

- For AXCL 1225 and 1500, the impellers to be molded FRP, backward inclined.  The impellers of the AXCL 1825 and larger to be airfoil, backward inclined, manufactured in solid FRP, unitary construction, with smooth surfaces. A metal backplate integral to the FRP impeller and encapsulated in resin shall have the hub extending to the outside of the fan housing.  The shaft end in the housing to be covered by a tight fitting FRP cap.  Impellers manufactured in steel and coated with a plastic material are not acceptable.

- The impellers shall be electronically balanced both statically and dynamically Grade G6.3 per AMCA 204 Standard and conform to ASTM Standard D-4167.

2.04 FAN MOTORS AND DRIVE.

- Motors to be premium efficiency, standard NEMA frame, 1800 RPM ( Belt Drive) or 900, 1200, or 1800 RPM (Direct Drive), TEFC with a 1.15 service factor.

- A factory mounted NEMA 3R disconnect switch shall be provided for each fan.

- Belt drive units shall have belts and sheaves sized for 150% of the fan operating brake horsepower, and shall be readily and easily accessible for service.

- Drives up to 5 HP shall be provided with variable pitch sheave.

- Shaft to be ANSI C-1045 steel, and be protected with TECTYL 822B protective coating.

- Shafts to be AISI -1045 carbon steel. The shaft shall not be in the corrosive air stream.

- Belt driven AXCL fans shall have shaft bearings sized for a minimum life of  L-10 100,000 hours. Bearings shall be ball or spherical pillow block type, sealed to retain lubricant and exclude dust and air.  Due to the bifurcated fan housing design, bearing inspection and relubrication shall be accomplished without fan disassembly, and in clear view, without the use of extended lube lines.

- Belt drive guards and motor covers shall be supplied, as indicated on the schedule.

PART 3  INSTALLATION

- Install fans as indicated, with resilient mountings and flexible electrical leads.

- Pipe housing drain to nearest drain.

- Install fans in accordance with manufacturers instructions.

PART 4  ACCEPTABLE MANUFACTURERS

- M. K. Plastics Corporation, model AXCL FRP Bifurcated Inline Centrifugal Fan.

- Approved equal.