PART 1 GENERAL

1.01 WORK INCLUDED

- Fiberglass Reinforced Plastic (FRP), inline centrifugal fan.

1.02 RELATED WORK

- All sections, drawing plans, specifications and contract documents.

1.03 REFERENCES

- AMCA -99 Standards Handbook

- AMCA 210 - Laboratory Methods of Testing Fans for Rating Purposes.

- AMCA 211 - Certified Ratings Procedure.

- AMCA 300 - Test Code for Sound Rating Air Moving Devices.

- AMCA 311 - Certified Sound Ratings Program for Air Moving Devices.

- AFMBA - Method of Evaluating Load Ratings of Bearings (ASA - B3.11).

- AMCA 204 - Balance Quality and Vibration Levels for Fans.

- ASTM D4167-97 – Standard Specification for Fiber-Reinforced Plastic Fans and Blowers.

1.04 QUALITY ASSURANCE

- Fans shall be tested in accordance with AMCA Standards 210 and 300, and performance ratings shall be submitted in conformance to AMCA Publications 211 and 311. Fans must be Licensed to Bear the AMCA Certified Ratings Seal for Sound and Air Performance. Acceptable manufacturers whose equipment is not licensed to bear the AMCA Certified Ratings Seal for Sound and Air Performance must submit air and sound performance tests conducted in accordance with AMCA Standards 210 and 300, in a registered AMCA test facility, and certified for accuracy (stamped) by a registered professional engineer.

- Classification for Spark Resistant Construction; Conform to AMCA 99.

- Each fan shall be tested before shipping. Motors to be tested for amperage drawn.

- A certificate to be supplied with each fan as to quality control before shipping and compliance to specifications.

1.05 SUBMITTALS

- Provide dimensional drawings and product data on each fan assembly.

- Provide fan curves for each fan at the specified operation point, with the flow, static pressure and horsepower clearly plotted.

- Provide inlet sound power readings for the eight octave bands.

PART 2 PRODUCTS

2.01 GENERAL

- Performance is based at standard conditions (density 0.075 Lb/ft3).

- Fans selected shall be capable of accommodating static pressure and flow variations of +/-15% of scheduled values.

- Each fan shall be belt drive arrangement #9 or direct drive arrangement #4 in AMCA arrangements as stated in the specs or on the drawings.

- Fasteners to be 304 stainless steel.

2.02 FAN HOUSING

- Fan housing shall be of FRP tubular ‘split’ design, in which shaft and drives are protected from the corrosive, contaminated air stream. Housing as well as air inlet shall be aerodynamically designed for high-efficiency, engineered to reduce incoming air turbulence. Housings shall be resin rich to be smooth exterior and interior.

- Fan housing shall be manufactured in specifically formulated resins, for maximum corrosion resistance, UV inhibited and reinforced with fiberglass for structural strength. Fastening bolts holding the casing to the support plate are to be encapsulated in FRP. No uncoated metal fan parts in the corrosive air stream will be tolerated. Minimum casing wall thickness to be 1/4” on AXTC 1825 to AXTC 3650, and 5/16” on AXTC 4025 and larger. Fans to be supplied with an internal graphite liner and grounding strap, (when specified), to remove static electricity. Flame retardancy of 25 or less, is standard.

- Fan inlet & outlet to be flanged, minimum thickness 3/8”. Flange drilling to be MK Plastics standard size hole pattern.

- Split housing design to give easy access for impeller inspection and service.

- Shaft seal to be neoprene or Teflon (when specified).

- AXTC fans shall be supplied with horizontal or vertical mounting brackets, as stated and shown on the plans and specifications.

- Roof mounted exhaust fans shall be supplied with FRP curb caps and FRP discharge butterfly dampers, according to drawings, and shown on the plans and specifications.

- Roof mounted supply fans shall be supplied with FRP curb caps and FRP weather hood, according to drawings, and shown on the plans and specifications

- M. K. Plastics (when specified) will supply a Vacuum Hub Seal to avoid any contaminated air from escaping (patent pending)

- Finish color to be MK Plastics light gray.

2.03 FAN IMPELLER

- Impellers shall be centrifugal backward inclined, airfoil, vinyl ester fiberglass reinforced, Class II, specially designed to facilitate the flow through the casing for improved efficiency.

- The impellers shall be electronically balanced both statically and dynamically in accordance with ANSI/AMCA 204-96 “Balance Quality and Vibration Levels for Fans” to Fan Application Category BV-3, Balance Quality Grade G6.3. and conform to ASTM Standard D-4167.

2.04 FAN MOTORS AND DRIVE.

- Motors to be standard efficiency, standard NEMA frame, 1800 RPM (Belt Drive) or 900, 1200, or 1800 RPM (Direct Drive), TEFC with a 1.15 service factor.

- A factory mounted NEMA 3R disconnect switch can be provided for each fan, if indicated on the schedule.

- Belt drive units shall have belts and sheaves sized for 120% of the fan operating brake horsepower, and shall be readily and easily accessible for service.

- Drives up to 5 HP shall be provided with variable pitch sheave.

- Shaft to be ANSI C-1045 steel, and be protected with TECTYL 822B protective coating. The shaft shall not be in the corrosive air stream. 304 or 316 stainless steel shafts are available (when specified).

- Belt driven AXT fans shall have heavy duty, precision, bearings sized for L10 - 100,000 hours.  Bearings shall be ball or spherical pillow block type, sealed to retain lubricant and exclude dust and air.  Bearings shall have extended lube lines to allow for lubrication.

- FRP belt drive guards are standard. Motor covers shall be supplied, as per the specification.

- Bearing lubrication lines shall be extended to the exterior of the unit, on belt drive application.

PART 3 INSTALLATION

- Install fans as indicated, with resilient mountings and flexible electrical leads.

- Install fans in accordance with manufacturer’s instructions.

PART 4 ACCEPTABLE MANUFACTURERS

- M. K. Plastics Corporation, model AXTC tubular inline centrifugal fiberglass fan.

- Approved equal.