PART 1  GENERAL

1.01 WORK INCLUDED

- High-Plume Dilution Laboratory Exhaust Fans

1.02 RELATED WORK

- All sections, drawing plans, specifications and contract documents.

1.03 REFERENCES

- AMCA -99-10 Standards Handbook.

- AMCA 204-05 - Balance Quality and Vibration Levels for Fans.

- AMCA 205-12 – Energy Efficiency Classification for Fans.

- AMCA 210-07 - Laboratory Methods of Testing Fans for Aerodynamic Performance Rating.

- AMCA 211-13 – Certified Ratings Program - Product Rating Manual for Fan Air Performance.

- AMCA 260-13 - Laboratory Methods of Testing Induced Flow Fans for Rating.

- AMCA 300-08 - Reverberant Room Method for Sound Testing of Fans.

- AMCA 311-05 - Certified Ratings Program.

- AFMBA - Method of Evaluating Load Ratings of Bearings (ASA - B3.11).

- AMCA 500 - Test Methods for Louvers, Dampers and Shutters.

- SMACNA - Medium Pressure Plenum Construction Standard.

- ANSI Z9.5 - Laboratory Design.

- ASHRAE - Laboratory Design Guide.

1.04 QUALITY ASSURANCE

- Performance ratings: Conform to AMCA standard 205, 211, 260 and 311. All fans shall be licensed to bear the AMCA ratings seal for FEG ratings (AMCA 205), Air Performance (AMCA 210), Sound Performance (AMCA 300), and Induced Flow for high plume dilution fans (AMCA 260). Acceptable manufacturers whose equipment are not licensed to bear the AMCA seal for Sound, Air Performance and Induced Flow must submit performance tests conducted by an independent third party at a registered AMCA test facility, and certified for accuracy (stamped) by a registered professional engineer (at the manufacturers expense).

- Classification for Spark Resistant Construction Conform to AMCA 99.

- All fans prior to shipment shall be completely assembled and test run as a unit at the specified operating speed or maximum RPM allowed for the particular construction type. Each wheel shall be statically and dynamically balanced in accordance with ANSI/AMCA 204 “Balance Quality and Vibration Levels for Fans” to Fan Application Category BV-3, Balance Quality Grade G6.3. Balance readings shall be taken by electronic type equipment in the axial, vertical, and horizontal directions on each of the bearings. Records shall be maintained and a written copy shall be available upon request.

1.05 SUBMITTALS

- Provide dimensional drawings and product data on each high-plume dilution laboratory exhaust fan assembly.

- Provide fan curves for each fan at the specified operation point, with the flow, static pressure and horsepower clearly plotted.

- Provide nozzle velocity of exhaust fan, total exhaust flow, and discharge plume height at specified wind velocity.

- Strictly adhere to QUALITY ASSURANCE requirements of AMCA CERTIFICATION, as stated in section 1.04.A of this specification, and provide QC certificate as stated in section 1.04.C of this specification.

- Provide AMCA Certified FEG minimum acceptable rating values of FEG 63 (fan sizes 1500), FEG 67 (fan sizes 1825-2700), FEG 75 (fan sizes 3000-5425).

PART 2  PRODUCTS

2.01 GENERAL

- Base fan performance at standard conditions (density 0.075 Lb/ft3).

- Each fan shall be direct driven in AMCA arrangement 4 according to drawings.

- Fans to be equipped with lifting lugs.

- Fasteners to be 304 stainless steel.

2.02 CORROSION RESISTANT COATING

- All fan and plenum components shall be corrosion resistant coated with a two part electrostatically applied, baked, corrosion resistant, Plastifer™ Polyester powder coating system. Standard finish color to be M.K. Plastics light gray.

- All steel surfaces shall be cleaned and prepared using a multi-stage process that includes phosphate washing to increase corrosion resistance, surface area and improve paint adhesion.

- Coatings shall consist of a 70% zinc rich polyester primer and a polyester powder resin top coat that shall be electrostatically applied and cured. Final coating thickness shall be a minimum 4-6 mil for superior corrosion resistance, and shall include UV inhibitors to prevent chalking from sunlight.

- Note that fan housings that have 8-10 mil thick liquid coating are more subject to running or sagging, manually applied have a non-uniform coverage over the surface, final finish is less durable and is environmentally unfriendly due to the emission of volatile organic compounds (solvents).

2.03 FAN HOUSING AND OUTLET

- Fan housing to be aerodynamically designed with high-efficiency inlet, engineered to reduce incoming air turbulence.

- Fan housing shall be of heavy gauge, continuously welded construction. Housings with lock seams or partially welded construction are not acceptable. Housings shall be cylindrical, inlets shall be fully streamlined. Housings shall be suitably braced to prevent vibration or pulsation. Extended lube lines shall be provided for ease of lubrication to motor bearings.

- The entire fan assembly shall be thoroughly degreased and deburred before coating. Refer to specification section 2.02 for corrosion resistant coating. No uncoated metal fan parts will be allowed.

- A bifurcated fiberglass reinforced plastic (FRP) discharge nozzle shall be supplied by the fan   manufacturer and be designed to efficiently handle an outlet velocity of up to 7,000 FPM. The discharge shall include a venturi and  fiberglass wind band to induce ambient air up to 270% of fan capacity. All fiberglass parts shall include UV inhibitors in the resins to prevent chalking from the sunlight.

- Fan assembly shall be either AMCA type C or AMCA type B spark resistant construction, when noted on the schedule.

- Provide housing drain shall be provided for condensation and rainwater removal.

- A bolted access door shall be supplied for impeller inspection and service.

2.04 FAN IMPELLER

- Fan impeller shall be mixed flow design, (Axijet-VM), with non-stall characteristics for low to medium pressure applications.

- Mixed flow impellers shall have die-formed hollow airfoil blades designed for maximum efficiency, and quiet and stable operation. Blades shall be continuously welded to the back plate and wheel cone.

- All impellers shall be statically and dynamically balanced and the complete fan assembly including motor and drive shall be test balanced at or near the operating speed at the factory prior to shipment.

- Fan impeller shall be coated with a minimum of 4-6 mil electrostatically applied baked polyester powder coating. Refer to specification section 2.02 for corrosion resistant coating.

2.05 FAN INLET ELBOW/PLENUM

- For constant volume systems, the fan shall be connected directly to a roof curb and duct without the need of bypass damper.

- For variable volume systems, an inlet elbow/plenum shall be provided as shown on drawings. The elbow/plenum shall be equipped with a bypass air damper(s) and fiberglass reinforced plastic (FRP) weather cowl and birdscreen, for introducing outside air at roof level upstream of the fan. The plenum shall be constructed of galvanealed steel, comply with specification section 2.02 for corrosion resistant coating, and mounted on an insulated curb.

- Bypass air damper(s) shall be opposed-blade, airfoil design, extruded aluminum with a clear anodized finish (salt water resistance), with linkage hardware installed in the side frame. All aluminum linkage hardware parts shall be clear anodized and all non-aluminum linkage hardware parts shall be type 316 stainless steel. Dampers shall be suitable for applications up to 10 inches wg. in extruded aluminum. For higher pressures up to 20” wg., the damper blades and frame shall be heavy duty H.R. steel and polyester coated. Each bypass damper shall be housed inside a fiberglass reinforced plastic (FRP) weather cowl and birdscreen, to prevent the possibility of rainwater entrainment.

- Fan isolation damper(s) shall be parallel-blade, airfoil design, extruded aluminum with a clear anodized finish (salt water resistance), with linkage hardware installed in the side frame. All aluminum linkage hardware parts shall be clear anodized and all non-aluminum linkage hardware parts shall be type 316 stainless steel. Dampers shall be suitable for applications up to 10 inches wg. in extruded aluminum. For higher pressures up to 20” wg., the damper blades and frame shall be heavy duty H.R. steel and polyester coated. Each isolation damper shall be housed inside a polyester coated galvanealed steel enclosure, on top of the mixing plenum. Damper access and service, (including removal and replacement and drive actuators) shall be performed outside of the contaminated plenum interior.

- All dampers shall have an extended control shaft for electronic, pneumatic or manual control actuation.

2.06 FAN MOTORS AND DRIVE

- Motors to be premium efficiency, standard NEMA frame, 900, 1200, 1800 or 3500 RPM, TEFC with a 1.15 service factor. Motor mounting shall be “C-face” and / or foot mount.

- A factory mounted NEMA 3R disconnect switch shall be provided for each fan.

- Fans shall be AMCA arrangement 4, (as standard).

- All non-permanently lubricated motors shall have extended lube lines with zerk fittings.

PART 3  INSTALLATION

- Install fans as indicated on the contract drawings.

- Pipe housing drain to the nearest drain.

- Fan or Fan/Plenum assembly shall be mounted on a structural support curb with a specified height as shown on the drawings. Roof curb shall be insulated and fabricated of a minimum 14 Ga. structurally reinforced galvanized steel.

- Vibration isolation shall be limited to neoprene vibration pads.

- Install fans in accordance with manufacturer’s instructions, applicable specification and code requirements.

PART 4  ACCEPTABLE MANUFACTURERS

- M. K. Plastics Corporation, model Axijet-VM Direct-Drive High Plume Dilution Fan.

- Approved equal.