PART I GENERAL

1.01 WORK INCLUDED

- FRP Medium Pressure Centrifugal Fans.

1.02 RELATED WORK

- All sections, drawing plans, and contract documents.

1.03 REFERENCES

- AMCA -99-10 - Standards Handbook.

- AMCA 204-05 - Balance Quality and Vibration Levels for Fans.

- AMCA 205-12 – Energy Efficiency Classification for Fans.

- AMCA 210-07 - Laboratory Methods of Testing Fans for Aerodynamic Performance Rating.

- AMCA 211-13 – Certified Ratings Program - Product Rating Manual for Fan Air Performance.

- AMCA 260-13 - Laboratory Methods of Testing Induced Flow Fans for Rating.

- AMCA 300-08 - Reverberant Room Method for Sound Testing of Fans.

- AMCA 311-05 - Certified Ratings Program.

- AFMBA - Method of Evaluating Load Ratings of Bearings (ASA - B3.11).

- ASTM D4167-97 - Standard Specification for Fiber-Reinforced Plastic Fans and Blowers.

1.04 QUALITY ASSURANCE

- Performance ratings: Conform to AMCA standard 205, 211, and 311. All fans shall be licensed to bear the AMCA ratings seal for FEG ratings (AMCA 205), Air Performance (AMCA 210) and Sound Performance (AMCA 300).

- Classification for Spark Resistant Construction; Conform to AMCA 99.

- All fans prior to shipment shall be completely assembled and test run as a unit at the specified operating speed or maximum RPM allowed for the particular construction type. Each wheel shall be statically and dynamically balanced in accordance with ANSI/AMCA 204 “Balance Quality and Vibration Levels for Fans” to Fan Application Category BV-3, Balance Quality Grade G6.3. Balance readings shall be taken by electronic type equipment in the axial, vertical, and horizontal directions on each of the bearings. Records shall be maintained and a written copy shall be available upon request.

1.05 SUBMITTALS

- Provide dimensional drawings and product data on each CNW fan.

- Provide fan curves for each fan at the specified operating point, with the flow, static pressure and horsepower clearly plotted.

- Provide AMCA Certified FEG minimum acceptable rating values of the following:

  - FEG 67 (CNW 200 to CNW 315)

- Strictly adhere to QUALITY ASSURANCE requirements as stated in section 1.04 of this specification.

PART 2 EQUIPMENT

2.01 GENERAL

- Base fan performance at standard conditions (density 0.075 Lb/ft3)

- Fans selected shall be capable of accommodating static pressure and airflow of scheduled values.

- Each fan shall be belt drive in arrangement #10, direct drive arrangement #4 or according to drawings.

- Fasteners to be 304 stainless steel.

- UV inhibitors are added to the resins and are flame retardant class 1 of 25 or less.

2.02 FAN HOUSING

- Fan housing to be aerodynamically designed with high-efficiency inlet, engineered to reduce incoming air turbulence. Casings to be smooth exterior and resin rich interior.

- Fan housing shall be manufactured in specifically formulated resins, for maximum corrosion resistance, and reinforced with fiberglass for structural strength. Fastening bolts holding the casing to the support plate are to be encapsulated in FRP. No uncoated metal fan parts in the corrosive air stream will be tolerated.

- CNW fans to be supplied with a graphite liner and grounding strap to remove static electricity, if scheduled.

- Inside the casing, a FRP ridge to be attached to divert condensation from dripping over the hub.

- When specified, provide a casing drain attached to the casing at the lowest point for condensation removal.

- Fan outlet to be flanged. Fan inlet to be slip connection.

- An access door, when requested, shall be supplied for impeller inspection and service.

- Standard finish color to be light gray.

- Hub seal to be neoprene or Teflon (when required).

- M. K. Plastics when requested will supply a Vacuum Hub Seal to avoid any contaminated air from escaping (patent pending).

2.03 FAN IMPELLER

- Impellers should be solid molded FRP With radial tip curved  blades. FRP hub to have a tight fitting cap to protect shaft end. The hub to extend outside the casing. Impellers manufactured in steel and coated with a plastic material are not acceptable. All wheels shall be statically and dynamically balanced on precision electronic balancers to a Balance Quality Grade G6.3 per ANSI/AMCA 204 or better.

2.04 BASE SUPPORT

- Arr. #10 support to be manufactured in formed steel and to be baked polyester coated. Arr. #4 support to be FRP, depending on motor size.

- An access panel to be standard to provide accessibility to the motor junction box.

- An FRP weather cover to be provided with adequate motor ventilation.

2.05 FAN MOTORS AND DRIVES

- Motors to be TEFC with a 1.15 service factor, or accordance to fan schedule.

- Belts and pulleys are to be accessible for service and maintenance.

- CNW fans to have self-lube, cast iron, pillow block bearings.

- Shafts to be AISI -1045 carbon steel. The shaft shall not be in the corrosive air stream.

- All bearings to have a minimum L-10 life of 200,000 hours life.

- Drive guard to be supplied and manufactured according to OSHA standards.

- Motor sheaves shall be cast iron, variable pitch on applications 5 HP and smaller, and fixed pitch on 7.5 HP and larger.

2.06 ACCEPTABLE MANUFACTURERS

- M.K. Plastics Corporation, Model CNW.

- Approved Equal.