PART 1 GENERAL

  - REFERENCES

A.	AMCA 500 - Test Methods for Louvers, Dampers and Shutters.

B.	AMCA 511 - Certified Ratings Program for Air Control Devices.

  - SUBMITTALS

A.	Submit manufacturer's product data.

1.	Include leakage, pressure drop, and maximum pressure data.

2.	Indicate materials, construction, dimensions, and installation details.

3.	Verify damper leakage rating AMCA certified.

4.	Verify damper pressure drop ratings based on tests and procedures performed in accordance with AMCA 500.

  - QUALITY ASSURANCE

- Damper Capacity:  Demonstrate damper capacity to withstand HVAC system operating conditions.

- Pressure Drop Ratings:  Damper pressure drop ratings based on tests and procedures performed in accordance with AMCA 500.

- Leakage Rating:  Damper leakage rating AMCA certified.  Damper licensed to bear AMCA Certified Ratings Seal in accordance with AMCA 511. AMCA Certified Ratings Seal applies to air leakage performance.

  - DELIVERY & STORAGE

- Delivery: Deliver materials to site in manufacturer's original, unopened containers and packaging, with labels clearly indicating manufacturer and material.

- Storage: Store materials in a dry area indoors, protected from damage and in accordance with manufacturer's instructions.

- Handling: Handle and lift dampers in accordance with manufacturer's instructions. Protect materials and finishes during handling and installation to prevent damage.

PART 2 PRODUCTS

  - MANUFACTURER

A.	M.K. Plastics Corporation, model K-PD or equivalent.

  - FIBERGLASS CONTROL DAMPERS

- Furnish and install FRP control dampers, as shown on plans or as described in the schedule as per following specifications.

- Dampers shall comply with ASTM D4385-84A standards and frames, blades and axles should be of pultruded FRP construction.

- Resin used shall be flame retardant vinyl ester. Frames shall be 6” wide C-channel type with 3/16” wall thickness. Damper blades with smooth AIR FLOW SHAPE shall be hollow, 6-5/8” wide, with minimum 1/8” walls and center reinforced area. Blade edge must have a pultruded T slot to receive a silicone rubber extrusion to provide a double air seal. Blade ends to have a VITON cap (patent pending) to seal the space between blade and frame.

- Dampers shall be either parallel blade or opposed blade type, as noted on the schedule.

- Damper axles shall be minimum 304 stainless steel rods with one control rod (shaft) extending 6” outside the damper frame. Control actuation shall be either manual crank lever, hand quadrant, electric or pneumatic, as specified. Bearings shall be Teflon molded thermoplastic, design based on system pressure. Blade linkage shall be out of the air stream within the “C” channel frame.

- Fasteners, if provided, should be in 316 stainless steel.

PART 3 EXECUTION

3.1  EXAMINATION

- Inspect areas to receive dampers.  Notify the Engineer of conditions that would adversely affect the installation or subsequent utilization of the dampers. Do not proceed with installation until unsatisfactory conditions are corrected.

3.2  INSTALLATION

- Install dampers at locations indicated on the drawings and in accordance with manufacturer's installation instructions.

- Install dampers square and free from racking with blades running [horizontally] [vertically].

- Do not compress or stretch damper frame into duct or opening.

- Handle damper using [sleeve or] frame. Do not lift damper by the blades, actuator or jackshaft.

- Install bracing for multiple section assemblies to support assembly weight and to hold against system pressure. Install bracing as needed.