PART 1  GENERAL

1.01 WORK INCLUDED

- High-Plume Laboratory Exhaust Fans

1.02 RELATED WORK

- All sections, drawing plans, specifications and contract documents.

1.03 REFERENCES

- AMCA -99 Standards Handbook.

- AMCA 210-99 - Laboratory Methods of Testing Fans for Aerodynamic Performance Rating.

- AMCA 300-05 - Reverberant Room Method for Sound Testing of Fans.

- AFMBA - Method of Evaluating Load Ratings of Bearings (ASA - B3.11).

- AMCA 204-05 - Balance Quality and Vibration Levels for Fans.

- AMCA 500 - Test Methods for Louvers, Dampers and Shutters.

- SMACNA - Medium Pressure Plenum Construction Standard.

- ANSI Z9.5 - Laboratory Design.

- ASHRAE - Laboratory Design Guide.

1.04 QUALITY ASSURANCE

- Fans shall be tested in accordance with AMCA Standards 210 and 300.

- Classification for Spark Resistant Construction Conform to AMCA 99.

- All fans prior to shipment shall be completely assembled and test run as a unit at the specified operating speed or maximum RPM allowed for the particular construction type. Each wheel shall be statically and dynamically balanced in accordance with ANSI/AMCA 204 “Balance Quality and Vibration Levels for Fans” to Fan Application Category BV-3, Balance Quality Grade G6.3. Balance readings shall be taken by electronic type equipment in the axial, vertical, and horizontal directions on each of the bearings. Records shall be maintained and a written copy shall be available upon request.

1.05 SUBMITTALS

- Provide dimensional drawings and product data on each high-plume laboratory exhaust fan assembly.

- Provide fan curves for each fan at the specified operation point, with the flow, static pressure and horsepower clearly plotted.

- Provide nozzle velocity of exhaust fan, and discharge plume height at specified wind velocity.

- Strictly adhere to quality assurance, as stated in section 1.04 of this specification.

PART 2  PRODUCTS

2.01 GENERAL

- Base fan performance at standard conditions (density 0.075 Lb/ft3).

- Each fan shall be belt driven in AMCA arrangement 9 according to drawings.

- Fans to be equipped with lifting lugs.

- Fasteners to be 304 stainless steel.

2.02 CORROSION RESISTANT COATING

- All fan and plenum components shall be corrosion resistant coated with a two part electrostatically applied, baked, corrosion resistant, Plastifer™ Polyester powder coating system. Standard finish color to be M.K. Plastics light gray.

- All steel surfaces shall be cleaned and prepared using a multi-stage process that includes phosphate washing to increase corrosion resistance, surface area and improve paint adhesion.

- Coatings shall consist of a 70% zinc rich polyester primer and a polyester powder resin top coat that shall be electrostatically applied and cured. Final coating thickness shall be a minimum 4-6 mil for superior corrosion resistance, and shall include UV inhibitors to prevent chalking from sunlight.

- Note that fan housings that have 8-10 mil thick liquid coating are more subject to running or sagging, manually applied have a non-uniform coverage over the surface, final finish is less durable and is environmentally unfriendly due to the emission of volatile organic compounds (solvents).

2.03 FAN HOUSING AND OUTLET

- Fan housing to be aerodynamically designed with high-efficiency inlet, engineered to reduce incoming air turbulence.

- Fan housing shall be of heavy gauge, continuously welded construction. Housings with lock seams or partially welded construction are not acceptable. Housings shall be cylindrical, inlets shall be fully streamlined. Housings shall be suitably braced to prevent vibration or pulsation. Totally enclosed belt guard shall enclose motor sheave and V-belt drives. Extended lube lines shall be provided for ease of lubrication.

- The entire fan assembly, excluding the shaft, shall be thoroughly degreased and deburred before coating. Refer to specification section 2.02 for corrosion resistant coating. No uncoated metal fan parts will be allowed.

- A high velocity conical discharge nozzle shall be supplied by the fan manufacturer and be designed to efficiently handle an outlet velocity of up to 6000 FPM.

- Fan assembly shall be either AMCA type C or AMCA type B spark resistant construction, when noted on the schedule.

- Provide housing drain shall be provided for condensation and rainwater removal.

- A bolted access door shall be supplied for impeller inspection and service.

2.04 FAN IMPELLER

- Fan impeller shall be centrifugal flow type, non-overloading and shall have single thickness plate-type blades on sizes 1225 to 1500, and die-formed airfoil blades on 1825 and larger. Blades shall be continuously welded to the back plate and wheel cone. The back plate of the impeller shall be designed to offer lower resistance to the air leaving the impeller.

- All impellers shall be statically and dynamically balanced and the complete fan assembly including motor and drive shall be test balanced at or near the operating speed at the factory prior to shipment.

- Fan impeller shall be coated with a minimum of 4-6 mil electrostatically applied baked polyester powder coating. Refer to specification section 2.02 for corrosion resistant coating.

2.05 FAN INLET ELBOW/PLENUM

- For constant volume systems, the fan shall be connected directly to a roof curb and duct without the need of bypass damper.

- For variable volume systems, an inlet elbow/plenum shall be provided as shown on drawings. The elbow/plenum shall be equipped with a bypass air damper(s) and fiberglass reinforced plastic (FRP) weather cowl and birdscreen, for introducing outside air at roof level upstream of the fan. The plenum shall be constructed of galvanealed steel, comply with specification section 2.02 for corrosion resistant coating, and mounted on an insulated curb.

- Bypass air damper(s) shall be opposed-blade, airfoil design, extruded aluminum with a clear anodized finish (salt water resistance), with linkage hardware installed in the side frame. All aluminum linkage hardware parts shall be clear anodized and all non-aluminum linkage hardware parts shall be type 316 stainless steel. Dampers shall be suitable for applications up to 10 inches wg. in extruded aluminum. For higher pressures up to 20” wg., the damper blades and frame shall be heavy duty H.R. steel and polyester coated. Each bypass damper shall be housed inside a fiberglass reinforced plastic (FRP) weather cowl and birdscreen, to prevent the possibility of rainwater entrainment.

- Fan isolation damper(s) shall be parallel-blade, airfoil design, extruded aluminum with a clear anodized finish (salt water resistance), with linkage hardware installed in the side frame. All aluminum linkage hardware parts shall be clear anodized and all non-aluminum linkage hardware parts shall be type 316 stainless steel. Dampers shall be suitable for applications up to 10 inches wg. in extruded aluminum. For higher pressures up to 20” wg., the damper blades and frame shall be heavy duty H.R. steel and polyester coated. Each isolation damper shall be housed inside a polyester coated galvanealed steel enclosure, on top of the mixing plenum. Damper access and service, (including removal and replacement and drive actuators) shall be performed outside of the contaminated plenum interior.

- All dampers shall have an extended control shaft for electronic, pneumatic or manual control actuation.

2.06 FAN MOTORS AND DRIVE.

- Motors to be premium efficiency, standard NEMA frame, 1800 RPM, TEFC with a 1.15 service factor. A factory mounted NEMA 3R disconnect switch shall be provided for each fan. Motor maintenance shall be accomplished without fan impeller removal or requiring maintenance personnel to access the contaminated exhaust components.

- Fans submitted that use 900 RPM, 1200 RPM, or C-Face motors, shall include one spare motor per fan system, in accordance with ANSI Z9.5, section 4.14.7.4, CRITICAL SERVICE SPARES.

- Drive belts and sheaves shall be sized for 150% of the fan operating brake horsepower, and shall be readily and easily accessible for service, if required.

- Motor sheaves shall be cast iron, variable pitch on applications 5 HP and smaller, and fixed pitch on 7.5 HP and larger.

- Shaft to be ANSI C-1045 steel, and shall be coated with a black asphalt protectant.

- Bearings shall be heavy duty, grease lubricated, anti-friction ball or roller, self-aligning, pillow block type and selected for a minimum average bearing life (AFBMA L-10) in excess of 200,000 hours at the maximum fan RPM. Bearings shall be equipped with extended lubrication lines with grease fittings outside of the fan housing.

PART 3  INSTALLATION

- Install fans as indicated on the contract drawings.

- Pipe housing drain to the nearest drain.

- Fan or Fan/Plenum assembly shall be mounted on a structural support curb with a specified height as shown on the drawings. Roof curb shall be insulated and fabricated of a minimum 14 Ga. structurally reinforced galvanized steel.

- Vibration isolation shall be limited to neoprene vibration pads.

- Install fans in accordance with manufacturers instructions, applicable specification and code requirements.

PART 4  ACCEPTABLE MANUFACTURERS

- M. K. Plastics Corporation, model KVC Belt-Drive High Plume Fan.

- Approved equal.